## Designations 2027
Minimum-load assessment, spring 2027: Tallowbark Networks zone substations
Forecast for the 2027 reference Sunday (the 25 October 2026 reference day carried forward under framework section 3) with the solar soak from 1 September 2027. MW; negative demand is flow back into the subtransmission network.
Code | Zone substation | Threshold (MW) | Forecast lowest demand, 10.00 am to 3.00 pm (MW) | Designated | Solar to curtail at the lowest half-hour (MW) | Further inverter capacity before any half-hour falls below the threshold (MW) | Rooftop solar inverter capacity in service, 25 Oct 2026 (MW) | Of which the emergency backstop can curtail (MW)
BRM | Brindlemoor | -12.6 | -11.2 | No |  | 1.9 | 19.06 | 2.48
CRW | Corrowie | -7.7 | -5 | No |  | 3.7 | 11.41 | 1.26
GRB | Gerrimbal | -12.5 | -13.1 | Yes | 0.6 |  | 22.22 | 2.82
GNL | Goonellan | -11 | -8 | No |  | 4 | 16.09 | 2.34
KLB | Kellambie | -7.7 | -5.2 | No |  | 3.4 | 12.13 | 1.31
KNB | Kinnabar | -14.2 | -15.1 | Yes | 0.9 |  | 23.57 | 3.02
MDR | Mundaree | -7.3 | -8.4 | Yes | 1.1 |  | 15.66 | 1.86
ODR | Ondarra | -5.7 | -6.7 | Yes | 1 |  | 12.71 | 1.42
ORJ | Orrinjal | -5.6 | -3.7 | No |  | 2.6 | 8.46 | 1.11
PLD | Pelladrin | -7 | -4.8 | No |  | 2.9 | 8.99 | 1.06
QRB | Quorrabin | -9.9 | -10.6 | Yes | 0.7 |  | 18.66 | 2.56
TRV | Tarravine | -7.6 | -8.5 | Yes | 0.9 |  | 12.79 | 1.79
TBN | Tibbarin | -8.5 | -7.3 | No |  | 1.6 | 13.28 | 1.74
WDB | Wendimbra | -15.5 | -13.6 | No |  | 2.6 | 22.52 | 2.87
WRD | Wirrandel | -9 | -9.8 | Yes | 0.8 |  | 15.99 | 2.21
WYB | Wyndabar | -14.2 | -12.3 | No |  | 2.6 | 21.11 | 2.65
| Network |  |  | 7 of 16 |  |  | 254.64 | 32.5

## Basis
Item | Basis
Reference day | Sunday 25 October 2026: lowest network half-hour between 10.00 am and 3.00 pm of the spring 2026 Sundays, -153.3 MW (framework 2.2). SCADA converted from UTC to local time.
Solar to 1 Oct 2027 | Tallowbark outlook of 29 January 2027, priced at the 25 October output per kW of inverter capacity in the monitored sample (framework 3.1a).
Solar soak | Network notice NN-2027-02: switch-on signal by group from 10.00 am to noon, off at 4.00 pm. The signal reaches the 23,257 heaters whose meter's controlled-load contactor is driven by an integral audio-frequency receiver; the 8,575 heaters on meters with an internal time switch keep their overnight programme.
Heater draw | Each reached heater draws its element rating from its group's switch-on until it has taken its spring 2026 daily energy (controlled-load register kWh over days read, all of its meters; framework 3.2).
Thresholds | Framework section 4 (reviewed February 2026).
Solar in service | Applications chained through prior_application; the latest commissioned on or before 25 October 2026; NMIs with a meter in service that day; located by the metering register. Backstop: the inverter serial in service first commissioned on or after 1 July 2025 (framework 5.2).