## Return Q4 2027
Six treated-water ammonia channels flagged for the fourth quarter of 2027
Online monitoring return, WQ-DS-04 section 7. Prepared by Water Quality Compliance, Fernvale District Council, January 2028.
Item (a): flagged channel | Plant | Water | Analyser | Reads
BRN-FW1 | Brannock | Final | AQ-BRN-NH3 | High
CAL-FI1 | Calderwood | Filtered | AQ-CAL-NH3 | Low
DUN-FW1 | Dunmere | Final | AQ-DUN-NH3 | High
ELS-FW1 | Elstow | Final | AQ-ELS-NH3 | High
GAR-FI1 | Garrick | Filtered | AQ-GAR-NH3 | High
GAR-FW1 | Garrick | Final | AQ-GAR-NH3 | High
Plant | Item (b): filtered and final water samples analysed more than 24 h after collection | Item (c): hours at the fixed chlorine dose, filtered water ammonia reading not available
Ashcombe | 14 | 31.2
Brannock | 9 | 27.8
Calderwood | 8 | 35.8
Dunmere | 12 | 32.2
Elstow | 11 | 26.7
Fenwick | 13 | 34.8
Garrick | 14 | 31.3
Holmedale | 11 | 29.3

## Channels
Channel | Plant | Water | Carryover (mg/L as N) | Calibration error at the channel's level (mg/L as N) | Sample line (mg/L as N) | Offset (mg/L as N) | Flagged
ASH-FI1 | Ashcombe | Filtered | 0.0001 | 0 | 0 | 0.0001 | No
ASH-FW1 | Ashcombe | Final | 0.0011 | 0 | 0 | 0.0011 | No
BRN-FI1 | Brannock | Filtered | -0.0003 | 0 | 0 | -0.0003 | No
BRN-FW1 | Brannock | Final | 0.0115 | 0 | 0 | 0.0115 | Yes
CAL-FI1 | Calderwood | Filtered | 0.0014 | -0.0008 | -0.0104 | -0.0098 | Yes
CAL-FW1 | Calderwood | Final | 0.0003 | -0.0015 | 0 | -0.0012 | No
DUN-FI1 | Dunmere | Filtered | 0.0001 | 0 | 0 | 0.0001 | No
DUN-FW1 | Dunmere | Final | 0.0122 | 0 | 0 | 0.0122 | Yes
ELS-FI1 | Elstow | Filtered | -0.0004 | 0 | 0 | -0.0004 | No
ELS-FW1 | Elstow | Final | 0.0091 | 0 | 0 | 0.0091 | Yes
FEN-FI1 | Fenwick | Filtered | 0.0003 | 0 | 0 | 0.0003 | No
FEN-FW1 | Fenwick | Final | 0.0007 | 0 | 0 | 0.0007 | No
GAR-FI1 | Garrick | Filtered | 0.0267 | 0 | 0 | 0.0267 | Yes
GAR-FW1 | Garrick | Final | 0.0112 | 0 | 0 | 0.0112 | Yes
HOL-FI1 | Holmedale | Filtered | 0.0255 | -0.008 | -0.0192 | -0.0017 | No
HOL-FW1 | Holmedale | Final | 0.0079 | -0.008 | 0 | -0.0001 | No

## Analysers
Analyser | Plant | Carryover from the port before | Carryover from two ports before | Check mean, Q4 (mg/L as N) | Calibration error | Filtered sample line
AQ-ASH-NH3 | Ashcombe | under 0.01 | under 0.01 | 0.0996 | Within the checks' scatter | No change at the flushes
AQ-BRN-NH3 | Brannock | 0.072 | 0.019 | 0.1011 | Within the checks' scatter | No change at the flushes
AQ-CAL-NH3 | Calderwood | under 0.01 | under 0.01 | 0.0916 | Span error: shortfall in proportion | Takes about 60 per cent of the ammonia when grown; rises 0.009 to 0.011 at each monthly flush (six hours after, two days before)
AQ-DUN-NH3 | Dunmere | 0.078 | 0.019 | 0.0993 | Within the checks' scatter | No change at the flushes
AQ-ELS-NH3 | Elstow | 0.076 | 0.02 | 0.1002 | Within the checks' scatter | No change at the flushes
AQ-FEN-NH3 | Fenwick | under 0.01 | under 0.01 | 0.0996 | Within the checks' scatter | No change at the flushes
AQ-GAR-NH3 | Garrick | 0.066 | 0.019 | 0.1008 | Within the checks' scatter | No change at the flushes
AQ-HOL-NH3 | Holmedale | 0.07 | 0.02 | 0.092 | Zero error: the same shortfall at every level | Takes nearly all of the ammonia when grown; rises 0.018 to 0.020 at each monthly flush (six hours after, two days before)

## Notes
Offset: WQ-DS-04 section 3, the mean over the channel's readings held in the historian with quality G for the quarter (New Zealand time) of the reading less the ammonia in the water at its sample point; flagged beyond 0.005 mg/L as N either way (section 4).
Carryover: the cell does not empty between ports, so each reading is a mix of its own water with shares of the two samples before it. The shares are the analyser's, fitted once on both treated ports' readings against the readings of the two slots before them, each port with its own level and its own response to the raw water 2 to 8 hours earlier; the check cycles count as the cell's content. A slot the historian filled from the outstation after a failed poll counts by its G row.
Calibration: Holmedale and Calderwood read about 8 per cent low on the 0.100 standard. Against the raw grabs, with the raw port's own carryover from the treated ports ahead of it taken out, Holmedale reads the same 0.008 low (a zero error, carried whole to its treated channels) and Calderwood about 8 per cent low (a span error, about 0.001 at its treated levels).
Sample lines: the check standard enters at the check port, after the sample lines, and the laboratory's grabs come from the taps, so neither sees what a line takes. With carryover and calibration taken out, Calderwood's and Holmedale's filtered readings rise at every monthly line flush in the register's planned maintenance log and fall back over the following days as the unchlorinated line's film grows again (fitted on the days since the flush with the raw water's lagged response, regrowth time 2.0 days); averaged over the quarter's G readings their lines read 0.010 and 0.019 below the water. No other channel moves at the flushes.
Item (b): the laboratory's analysis stamps run behind its reception and release times (some runs are stamped up to 53 minutes before reception logged their bottles, and no result is released within 64 minutes of its stamp), so the stamps move forward an hour, the analyser keeping standard time against the daylight time of the other clocks; any shift in that range counts the same. October's treated samples are under the laboratory's old codes (its notice of 28 October 2027). Each bottle counts once: the 7 December round's treated bottles appear twice in the export, logged again on unpacking under the courier docket's pickup time, with the same point, analysis stamp, result and release.
Item (c): the PLC reads the analyser directly, so a slot the historian lost, filled after a failed poll, or lost in a run of failed polls at every port that nothing filled, no technician's check followed and the analyser's port sequence ran through unbroken (the telemetry's, one a plant in November) was good at the plant. A run after which the sequence starts again at the raw water port is the analyser's own stop (each analyser once, on the storm night of 26 to 27 October or 3 to 4 December, until the morning reset), and a filtered port's own run of F rows, with the other ports read between them, is a reading that never reached the PLC (once at each plant); both count with the analyser's faults and its check cycles, each gap beyond the two-hour hold.