## Conversion 2027
2027 backbone conversion: customer-minutes of sustained interruption removed a year
2019 to 2025 outage record outside the accepted major event days; feeder breaker and line recloser tickets from vegetation, wind or wildlife, less those every feeder at the substation opened in the same minute; nine in ten, divided by seven.
Feeder | Substation | Backbone miles | Estimated cost (USD million) | Customer-minutes removed a year | Value a year at USD 2.10 (USD)
F-205 | Sorrel Hill | 14.4 | 6 | 237600 | 499000
F-112 | Pell Creek | 12.6 | 5.3 | 137800
F-301 | Byers Mill | 14.2 | 6 | 67300
F-208 | Sorrel Hill | 12.4 | 5.2 | 39000
F-303 | Byers Mill | 10.5 | 4.4 | 32100
F-114 | Pell Creek | 11.2 | 4.7 | 29600
Recommended: F-205 (Sorrel Hill).

## Storm days 2023-25
Customers' record on the commission's accepted major event days of 2023 to 2025
Tickets that began on an accepted major event day (Eastern). Restoration: the crew's Restored status where the storm crews' records hold the ticket (contract crews' devices on Eastern standard time), otherwise the outage system's restoration.
Feeder | Substation | Customer-minutes | Customers interrupted | Minutes per customer interrupted
F-112 | Pell Creek | 11615000 | 28199 | 411.9
F-114 | Pell Creek | 5773000 | 16993 | 339.7
F-205 | Sorrel Hill | 7332000 | 18634 | 393.5
F-208 | Sorrel Hill | 6210000 | 15019 | 413.5
F-301 | Byers Mill | 9952000 | 24504 | 406.1
F-303 | Byers Mill | 4391000 | 10448 | 420.3

## Taps 2019-25
Interruptions the tap fuses cleared outside the major event days, 2019 to 2025
Fuse tickets that did not begin on an accepted major event day. Legacy tickets entered from the trouble crews' handhelds: durations read as hours and minutes, dates as the day the ticket closed.
Feeder | Substation | Customer-minutes a year | Minutes per customer interrupted
F-112 | Pell Creek | 23840 | 125.1
F-114 | Pell Creek | 14450 | 116.3
F-205 | Sorrel Hill | 25950 | 119.2
F-208 | Sorrel Hill | 9000 | 116.5
F-301 | Byers Mill | 16410 | 110.6
F-303 | Byers Mill | 13540 | 118.5