## 2027 program
2027 group driver replacement: P1, P3, P5, P7 and P9 go in, 20,922 luminaires
Tallisford Power & Light street lighting. Program test of Program Note SL-LM-04 rev. 3: work-management record closed 31 December 2026, luminaires on their original driver on 1 January 2027, failure before the twelfth anniversary of installation.
Phase | Installed | Original-driver failures to 31 Dec 2026 | On original driver 1 Jan 2027 | of which Vantrel Power Systems | of which Corvane Electronics | Projected share failing before year 12 | 2027 program
P1 | 4320 | 464 | 3624 | 2537 | 1087 | 60% | Yes
P2 | 3921 | 199 | 3549 | 1278 | 2271 | 30% | No
P3 | 5139 | 362 | 4573 | 3725 | 848 | 70% | Yes
P4 | 4465 | 111 | 4180 | 1746 | 2434 | 35% | No
P5 | 4025 | 106 | 3786 | 2591 | 1195 | 60% | Yes
P6 | 5540 | 35 | 5348 | 1007 | 4341 | 15% | No
P7 | 4264 | 45 | 4113 | 3122 | 991 | 65% | Yes
P8 | 3674 | 6 | 3593 | 576 | 3017 | 15% | No
P9 | 4918 | 14 | 4826 | 3422 | 1404 | 60% | Yes
P10 | 3420 | 1 | 3375 | 544 | 2831 | 15% | No
Program |  |  | 20922 |  |  |  | 5 phases
Shares to the nearest 5 per cent; a phase enters above 45 per cent (note 2.1). Each luminaire is projected under its own driver maker's lifetime (sheet Driver lifetimes), the maker read from its delivery lot's certificate of conformance.
Source: Brayle Electric installation logs 2021 to 2025; Halberd certificates of conformance; legacy WMS export to June 2023 and EAM work orders to 31 December 2026.

## Driver lifetimes
Original-driver lifetimes by driver maker, Weibull by maximum likelihood with suspensions
Driver maker | Drivers installed | Failures to 31 Dec 2026 | Weibull shape | Characteristic life (years) | Failed by year 12
Vantrel Power Systems | 22646 | 1327 | 3.3 | 9.8 | 85.87%
Corvane Electronics | 21040 | 16 | no wear-out |  | under 1%
One Weibull over every conversion driver expects more than 500 failures among Corvane Electronics' drivers by 31 December 2026, against the 16 recorded.

## Towns 2026
Converted poles' 2026 energy saving and the 72-hour repair standard, by town
Town | Energy saved against the sodium fixtures (MWh) | Outages repaired in 2026 | Missed the 72-hour standard
Ambrosine | 1824 | 473 | 186
Corrinvale | 2263 | 528 | 187
Dalwinter | 1942 | 414 | 156
Fallowmere | 1684 | 443 | 153
Garrick Hollow | 1888 | 429 | 149
Halverne Bend | 2188 | 441 | 161
Kesterbrook | 2558 | 479 | 193
Larkhaven | 2304 | 380 | 133
Energy on Schedule SL's accounting (3.1, 3.2), each converted pole against the sodium fixture the installer took down, whole MWh. Repairs timed under 4.2 from the first report of the outage, any light on an underground circuit counting for a cable fault, or from the Company's own find.
Source: Schedule SL; Corrinvale networked lighting control records 2026; customer outage reports, December 2025 to December 2026; GIS register at 31 December 2026.