## Evaluation
Kettle Ridge University Campus Water System (PWSID 4149327)
Source capacity evaluation for the 2026 sanitary survey: 1 October 2025 to 30 September 2026
Measure | Figure | Source
Maximum day (Eastern time, midnight to midnight) | 2026-08-20 | Daily use sheet
Water used on the maximum day (gal) | 4469527 | Production less storage change
Well production that day (gal) | 3716646 | Daily log, meter totalizers at 00:00
Water the four tanks gave up that day (gal) | 752881 | SCADA levels at 00:00 x gallons per foot
Maximum day demand (gpm) | 3103.8382 | Gallons a day / 1,440
Firm capacity (gpm) | 2920 | Wells sheet
Well capacity to add before 1 June 2027 (gpm) | 184 | Rounded up to a whole gpm
Firm capacity is the total of the wells' most recent pump-test capacities less Well 1, the largest: W1 1,090, W2 820, W3 760, W4 700, W5 640 gpm.
Maximum day demand is the day's well production less the water the four tanks gained between that day's midnights (here they gave water up), counting water lost from the mains as used.
The largest day of well production alone was August 21 (4,136,417 gal), when the wells refilled the tanks.

## Daily use
Date | Well production (gal) | Storage at 00:00 (gal) | Storage change (gal) | Water used (gal)
2025-10-01 | 3305564 | 3466067 | 6435 | 3299129
2025-10-02 | 3364630 | 3472502 | -14764 | 3379394
2025-10-03 | 3257701 | 3457738 | 26823 | 3230878
2025-10-04 | 2699737 | 3484561 | -151511 | 2851248
2025-10-05 | 2895544 | 3333050 | -42660 | 2938204
2025-10-06 | 3377914 | 3290390 | 187930 | 3189984
2025-10-07 | 3236549 | 3478320 | -36188 | 3272737
2025-10-08 | 3277195 | 3442132 | 6833 | 3270362
2025-10-09 | 3254779 | 3448965 | 6980 | 3247799
2025-10-10 | 3283450 | 3455945 | 2109 | 3281341
2025-10-11 | 2683872 | 3458054 | -57369 | 2741241
2025-10-12 | 2784775 | 3400685 | -31432 | 2816207
2025-10-13 | 3343976 | 3369253 | 101881 | 3242095
2025-10-14 | 3265284 | 3471134 | -31550 | 3296834
2025-10-15 | 3296060 | 3439584 | 18577 | 3277483
2025-10-16 | 3180521 | 3458161 | 26069 | 3154452
2025-10-17 | 3227308 | 3484230 | -22665 | 3249973
2025-10-18 | 2720318 | 3461565 | -208318 | 2928636
2025-10-19 | 2907143 | 3253247 | 104974 | 2802169
2025-10-20 | 3297394 | 3358221 | 115823 | 3181571
2025-10-21 | 3212309 | 3474044 | 27343 | 3184966
2025-10-22 | 3197396 | 3501387 | -32884 | 3230280
2025-10-23 | 3214167 | 3468503 | -21600 | 3235767
2025-10-24 | 3194937 | 3446903 | 397 | 3194540
2025-10-25 | 2730524 | 3447300 | -54895 | 2785419
2025-10-26 | 2784848 | 3392405 | -28434 | 2813282
2025-10-27 | 3268268 | 3363971 | 90043 | 3178225
2025-10-28 | 3248852 | 3454014 | -144 | 3248996
2025-10-29 | 3223101 | 3453870 | 18849 | 3204252
2025-10-30 | 3217861 | 3472719 | 6679 | 3211182
2025-10-31 | 3237969 | 3479398 | -38973 | 3276942
2025-11-01 | 2765659 | 3440425 | -147467 | 2913126
2025-11-02 | 2855258 | 3292958 | 92556 | 2762702
2025-11-03 | 3284745 | 3385514 | 72852 | 3211893
2025-11-04 | 3201561 | 3458366 | -37621 | 3239182
2025-11-05 | 3182321 | 3420745 | 62715 | 3119606
2025-11-06 | 3220184 | 3483460 | -63740 | 3283924
2025-11-07 | 3336825 | 3419720 | 15898 | 3320927
2025-11-08 | 2728900 | 3435618 | -93053 | 2821953
2025-11-09 | 2808619 | 3342565 | 110780 | 2697839
2025-11-10 | 3241851 | 3453345 | -5583 | 3247434
2025-11-11 | 3244059 | 3447762 | 59157 | 3184902
2025-11-12 | 3236193 | 3506919 | -9713 | 3245906
2025-11-13 | 3237276 | 3497206 | -27431 | 3264707
2025-11-14 | 3220395 | 3469775 | -299 | 3220694
2025-11-15 | 2723134 | 3469476 | -173992 | 2897126
2025-11-16 | 2864651 | 3295484 | 68164 | 2796487
2025-11-17 | 3158923 | 3363648 | -110208 | 3269131
2025-11-18 | 3311022 | 3253440 | 29897 | 3281125
2025-11-19 | 3236747 | 3283337 | -10422 | 3247169
2025-11-20 | 3254502 | 3272915 | 1753 | 3252749
2025-11-21 | 3271915 | 3274668 | 6153 | 3265762
2025-11-22 | 1609556 | 3280821 | -9449 | 1619005
2025-11-23 | 1616475 | 3271372 | 4296 | 1612179
2025-11-24 | 1894816 | 3275668 | -6428 | 1901244
2025-11-25 | 1899923 | 3269240 | 32837 | 1867086
2025-11-26 | 1942663 | 3302077 | 31285 | 1911378
2025-11-27 | 1825866 | 3333362 | -60469 | 1886335
2025-11-28 | 1946322 | 3272893 | 30132 | 1916190
2025-11-29 | 1465107 | 3303025 | -134690 | 1599797
2025-11-30 | 1746920 | 3168335 | 119557 | 1627363
2025-12-01 | 3115938 | 3287892 | -52499 | 3168437
2025-12-02 | 3257366 | 3235393 | 63001 | 3194365
2025-12-03 | 3201994 | 3298394 | -23791 | 3225785
2025-12-04 | 3282582 | 3274603 | -20020 | 3302602
2025-12-05 | 3296617 | 3254583 | 3527 | 3293090
2025-12-06 | 2724241 | 3258110 | -58939 | 2783180
2025-12-07 | 2796342 | 3199171 | -49253 | 2845595
2025-12-08 | 3372966 | 3149918 | 125141 | 3247825
2025-12-09 | 3306133 | 3275059 | -18791 | 3324924
2025-12-10 | 3302562 | 3256268 | -10103 | 3312665
2025-12-11 | 3280123 | 3246165 | 15842 | 3264281
2025-12-12 | 3321013 | 3262007 | 16220 | 3304793
2025-12-13 | 2668413 | 3278227 | 6813 | 2661600
2025-12-14 | 2664461 | 3285040 | -40718 | 2705179
2025-12-15 | 3150575 | 3244322 | 72486 | 3078089
2025-12-16 | 3073848 | 3316808 | -18551 | 3092399
2025-12-17 | 3069266 | 3298257 | -12926 | 3082192
2025-12-18 | 3072070 | 3285331 | -65433 | 3137503
2025-12-19 | 3089296 | 3219898 | 75925 | 3013371
2025-12-20 | 1336295 | 3295823 | -107355 | 1443650
2025-12-21 | 1467117 | 3188468 | -21128 | 1488245
2025-12-22 | 1902637 | 3167340 | 167337 | 1735300
2025-12-23 | 1694482 | 3334677 | -34996 | 1729478
2025-12-24 | 1697231 | 3299681 | -63821 | 1761052
2025-12-25 | 1698247 | 3235860 | -50063 | 1748310
2025-12-26 | 1860357 | 3185797 | 132242 | 1728115
2025-12-27 | 1302448 | 3318039 | -139290 | 1441738
2025-12-28 | 1462716 | 3178749 | -8860 | 1471576
2025-12-29 | 1867715 | 3169889 | 159128 | 1708587
2025-12-30 | 1710006 | 3329017 | -17925 | 1727931
2025-12-31 | 1676792 | 3311092 | -70641 | 1747433
2026-01-01 | 1849499 | 3240451 | 114026 | 1735473
2026-01-02 | 1675745 | 3354477 | -39325 | 1715070
2026-01-03 | 1299157 | 3315152 | -158678 | 1457835
2026-01-04 | 1388179 | 3156474 | -50490 | 1438669
2026-01-05 | 1951852 | 3105984 | 234622 | 1717230
2026-01-06 | 1692517 | 3340606 | -37527 | 1730044
2026-01-07 | 1717759 | 3303079 | -50743 | 1768502
2026-01-08 | 1709299 | 3252336 | -14954 | 1724253
2026-01-09 | 1807270 | 3237382 | 84290 | 1722980
2026-01-10 | 1312255 | 3321672 | -138603 | 1450858
2026-01-11 | 2803801 | 3183069 | -9054 | 2812855
2026-01-12 | 3294021 | 3174015 | 109625 | 3184396
2026-01-13 | 3290646 | 3283640 | -9502 | 3300148
2026-01-14 | 3251962 | 3274138 | -38695 | 3290657
2026-01-15 | 3320024 | 3235443 | 35348 | 3284676
2026-01-16 | 3296946 | 3270791 | -16807 | 3313753
2026-01-17 | 2720141 | 3253984 | -68573 | 2788714
2026-01-18 | 2796539 | 3185411 | -50618 | 2847157
2026-01-19 | 3390786 | 3134793 | 137739 | 3253047
2026-01-20 | 3260696 | 3272532 | 5517 | 3255179
2026-01-21 | 3291280 | 3278049 | -25027 | 3316307
2026-01-22 | 3344608 | 3253022 | -281708 | 3626316
2026-01-23 | 3520435 | 2971314 | 300872 | 3219563
2026-01-24 | 2704888 | 3272186 | -96436 | 2801324
2026-01-25 | 2807823 | 3175750 | -28938 | 2836761
2026-01-26 | 3345737 | 3146812 | 105904 | 3239833
2026-01-27 | 3308854 | 3252716 | -33913 | 3342767
2026-01-28 | 3290876 | 3218803 | 76529 | 3214347
2026-01-29 | 3180195 | 3295332 | -37623 | 3217818
2026-01-30 | 3311355 | 3257709 | 38326 | 3273029
2026-01-31 | 2689657 | 3296035 | -143419 | 2833076
2026-02-01 | 2816646 | 3152616 | -9105 | 2825751
2026-02-02 | 3334215 | 3143511 | 153472 | 3180743
2026-02-03 | 3261874 | 3296983 | -49747 | 3311621
2026-02-04 | 3237092 | 3247236 | -10035 | 3247127
2026-02-05 | 3323892 | 3237201 | 20377 | 3303515
2026-02-06 | 3260921 | 3257578 | 3277 | 3257644
2026-02-07 | 2720494 | 3260855 | -106534 | 2827028
2026-02-08 | 2842252 | 3154321 | -34588 | 2876840
2026-02-09 | 3409954 | 3119733 | 138808 | 3271146
2026-02-10 | 3258535 | 3258541 | -120 | 3258655
2026-02-11 | 3147074 | 3258421 | -45929 | 3193003
2026-02-12 | 3339188 | 3212492 | 36782 | 3302406
2026-02-13 | 3304952 | 3249274 | 22897 | 3282055
2026-02-14 | 2705689 | 3272171 | -135886 | 2841575
2026-02-15 | 2842113 | 3136285 | 16229 | 2825884
2026-02-16 | 3366521 | 3152514 | 139458 | 3227063
2026-02-17 | 3205897 | 3291972 | -16765 | 3222662
2026-02-18 | 3253832 | 3275207 | 20542 | 3233290
2026-02-19 | 3236004 | 3295749 | -3664 | 3239668
2026-02-20 | 3234324 | 3292085 | -65726 | 3300050
2026-02-21 | 2761347 | 3226359 | -90584 | 2851931
2026-02-22 | 2864383 | 3135775 | -17954 | 2882337
2026-02-23 | 3444406 | 3117821 | 157511 | 3286895
2026-02-24 | 3214382 | 3275332 | 5065 | 3209317
2026-02-25 | 3242586 | 3280397 | -14054 | 3256640
2026-02-26 | 3273744 | 3266343 | -97172 | 3370916
2026-02-27 | 3403836 | 3169171 | 75938 | 3327898
2026-02-28 | 2730962 | 3245109 | -122787 | 2853749
2026-03-01 | 2859885 | 3122322 | -215 | 2860100
2026-03-02 | 3407283 | 3122107 | 155974 | 3251309
2026-03-03 | 3216310 | 3278081 | -14897 | 3231207
2026-03-04 | 3272815 | 3263184 | 31212 | 3241603
2026-03-05 | 3239853 | 3294396 | -33022 | 3272875
2026-03-06 | 3293165 | 3261374 | 24084 | 3269081
2026-03-07 | 1709046 | 3285458 | -36525 | 1745571
2026-03-08 | 1770602 | 3248933 | 15878 | 1754724
2026-03-09 | 2070875 | 3264811 | -6535 | 2077410
2026-03-10 | 1958032 | 3258276 | -98795 | 2056827
2026-03-11 | 2159349 | 3159481 | 61334 | 2098015
2026-03-12 | 2141573 | 3220815 | 25491 | 2116082
2026-03-13 | 2091821 | 3246306 | 16392 | 2075429
2026-03-14 | 1773020 | 3262698 | 17472 | 1755548
2026-03-15 | 1793415 | 3280170 | 31604 | 1761811
2026-03-16 | 3243272 | 3311774 | -11112 | 3254384
2026-03-17 | 3195017 | 3300662 | -3393 | 3198410
2026-03-18 | 3277652 | 3297269 | -2766 | 3280418
2026-03-19 | 3245110 | 3294503 | -19027 | 3264137
2026-03-20 | 3259735 | 3275476 | 13815 | 3245920
2026-03-21 | 2689257 | 3289291 | -143871 | 2833128
2026-03-22 | 2829379 | 3145420 | -15627 | 2845006
2026-03-23 | 3396696 | 3129793 | 132522 | 3264174
2026-03-24 | 3259275 | 3262315 | 24011 | 3235264
2026-03-25 | 3192832 | 3286326 | -15048 | 3207880
2026-03-26 | 3236274 | 3271278 | 1011 | 3235263
2026-03-27 | 3304424 | 3272289 | 37823 | 3266601
2026-03-28 | 2667298 | 3310112 | -156612 | 2823910
2026-03-29 | 2812542 | 3153500 | -11620 | 2824162
2026-03-30 | 3550712 | 3141880 | 305782 | 3244930
2026-03-31 | 3220587 | 3447662 | 40358 | 3180229
2026-04-01 | 3214821 | 3488020 | -29153 | 3243974
2026-04-02 | 3273034 | 3458867 | -37111 | 3310145
2026-04-03 | 3255216 | 3421756 | 54477 | 3200739
2026-04-04 | 2685387 | 3476233 | -116809 | 2802196
2026-04-05 | 2798367 | 3359424 | 957 | 2797410
2026-04-06 | 3307931 | 3360381 | 77321 | 3230610
2026-04-07 | 3282742 | 3437702 | 29485 | 3253257
2026-04-08 | 3214550 | 3467187 | 446 | 3214104
2026-04-09 | 3245616 | 3467633 | -16959 | 3262575
2026-04-10 | 3246768 | 3450674 | 9218 | 3237550
2026-04-11 | 2686721 | 3459892 | -49991 | 2736712
2026-04-12 | 2756139 | 3409901 | -93972 | 2850111
2026-04-13 | 3431341 | 3315929 | 161793 | 3269548
2026-04-14 | 3228659 | 3477722 | -7927 | 3236586
2026-04-15 | 3300034 | 3469795 | -1268 | 3301302
2026-04-16 | 3275854 | 3468527 | -7684 | 3283538
2026-04-17 | 3288794 | 3460843 | 10424 | 3278370
2026-04-18 | 2678094 | 3471267 | -75158 | 2753252
2026-04-19 | 2746984 | 3396109 | -29701 | 2776685
2026-04-20 | 3414709 | 3366408 | 75211 | 3339498
2026-04-21 | 3316297 | 3441619 | 6189 | 3310108
2026-04-22 | 3312315 | 3447808 | -4101 | 3316416
2026-04-23 | 3261281 | 3443707 | -1961 | 3263242
2026-04-24 | 3272310 | 3441746 | 23220 | 3249090
2026-04-25 | 2659124 | 3464966 | -68117 | 2727241
2026-04-26 | 3037814 | 3396849 | 78261 | 2959553
2026-04-27 | 3160820 | 3475110 | 37910 | 3122910
2026-04-28 | 3173209 | 3513020 | -43816 | 3217025
2026-04-29 | 3218370 | 3469204 | -5112 | 3223482
2026-04-30 | 3215581 | 3464092 | -7990 | 3223571
2026-05-01 | 3230175 | 3456102 | 34683 | 3195492
2026-05-02 | 2599230 | 3490785 | -50896 | 2650126
2026-05-03 | 2668233 | 3439889 | 26145 | 2642088
2026-05-04 | 2970867 | 3466034 | -31375 | 3002242
2026-05-05 | 3199124 | 3434659 | 68615 | 3130509
2026-05-06 | 3120631 | 3503274 | 4818 | 3115813
2026-05-07 | 2905254 | 3508092 | -102954 | 3008208
2026-05-08 | 3185382 | 3405138 | 102069 | 3083313
2026-05-09 | 1738012 | 3507207 | -104672 | 1842684
2026-05-10 | 2038523 | 3402535 | 89535 | 1948988
2026-05-11 | 2035777 | 3492070 | -105979 | 2141756
2026-05-12 | 2180125 | 3386091 | 23225 | 2156900
2026-05-13 | 2128457 | 3409316 | -4554 | 2133011
2026-05-14 | 2115220 | 3404762 | 3879 | 2111341
2026-05-15 | 2111805 | 3408641 | -10953 | 2122758
2026-05-16 | 1965789 | 3397688 | 9067 | 1956722
2026-05-17 | 1836555 | 3406755 | 37102 | 1799453
2026-05-18 | 2145339 | 3443857 | -51889 | 2197228
2026-05-19 | 2173400 | 3391968 | 22515 | 2150885
2026-05-20 | 2170588 | 3414483 | -21769 | 2192357
2026-05-21 | 2187863 | 3392714 | -20943 | 2208806
2026-05-22 | 2101312 | 3371771 | 21617 | 2079695
2026-05-23 | 2017806 | 3393388 | 74500 | 1943306
2026-05-24 | 1949688 | 3467888 | -80331 | 2030019
2026-05-25 | 2171247 | 3387557 | 10913 | 2160334
2026-05-26 | 2327231 | 3398470 | -66475 | 2393706
2026-05-27 | 2265143 | 3331995 | 67539 | 2197604
2026-05-28 | 2196820 | 3399534 | -29795 | 2226615
2026-05-29 | 2364318 | 3369739 | -25696 | 2390014
2026-05-30 | 2080971 | 3344043 | 43394 | 2037577
2026-05-31 | 2082650 | 3387437 | -12231 | 2094881
2026-06-01 | 2182153 | 3375206 | -41369 | 2223522
2026-06-02 | 2601168 | 3333837 | 180191 | 2420977
2026-06-03 | 2221588 | 3514028 | -174277 | 2395865
2026-06-04 | 2226460 | 3339751 | 39501 | 2186959
2026-06-05 | 2620457 | 3379252 | 71684 | 2548773
2026-06-06 | 2107024 | 3450936 | 13379 | 2093645
2026-06-07 | 2104595 | 3464315 | -75211 | 2179806
2026-06-08 | 2567986 | 3389104 | 103941 | 2464045
2026-06-09 | 2482255 | 3493045 | -2981 | 2485236
2026-06-10 | 2506200 | 3490064 | -2620 | 2508820
2026-06-11 | 2240830 | 3487444 | -154901 | 2395731
2026-06-12 | 2392928 | 3332543 | 49851 | 2343077
2026-06-13 | 2115766 | 3382394 | -19822 | 2135588
2026-06-14 | 2087285 | 3362572 | 19565 | 2067720
2026-06-15 | 2463064 | 3382137 | -55998 | 2519062
2026-06-16 | 2728078 | 3326139 | 125059 | 2603019
2026-06-17 | 2548222 | 3451198 | 33288 | 2514934
2026-06-18 | 2154666 | 3484486 | -107516 | 2262182
2026-06-19 | 2404440 | 3376970 | 15535 | 2388905
2026-06-20 | 2011306 | 3392505 | -938 | 2012244
2026-06-21 | 2111790 | 3391567 | -31306 | 2143096
2026-06-22 | 2499546 | 3360261 | 149498 | 2350048
2026-06-23 | 2219867 | 3509759 | -184229 | 2404096
2026-06-24 | 2709752 | 3325530 | 128188 | 2581564
2026-06-25 | 2418251 | 3453718 | 55759 | 2362492
2026-06-26 | 2665408 | 3509477 | -47265 | 2712673
2026-06-27 | 2110600 | 3462212 | -60660 | 2171260
2026-06-28 | 2180810 | 3401552 | -20504 | 2201314
2026-06-29 | 2516878 | 3381048 | 124488 | 2392390
2026-06-30 | 2179499 | 3505536 | -172798 | 2352297
2026-07-01 | 3099066 | 3332738 | 148850 | 2950216
2026-07-02 | 2377602 | 3481588 | 31770 | 2345832
2026-07-03 | 2499987 | 3513358 | -45692 | 2545679
2026-07-04 | 2226985 | 3467666 | -165849 | 2392834
2026-07-05 | 2320000 | 3301817 | 15037 | 2304963
2026-07-06 | 2596555 | 3316854 | 194421 | 2402134
2026-07-07 | 2653192 | 3511275 | -20615 | 2673807
2026-07-08 | 2486718 | 3490660 | 15000 | 2471718
2026-07-09 | 2531265 | 3505660 | -46168 | 2577433
2026-07-10 | 2573371 | 3459492 | -2355 | 2575726
2026-07-11 | 2243641 | 3457137 | -158087 | 2401728
2026-07-12 | 2300781 | 3299050 | 67275 | 2233506
2026-07-13 | 2811391 | 3366325 | 94405 | 2716986
2026-07-14 | 2709448 | 3460730 | 12484 | 2696964
2026-07-15 | 2526350 | 3473214 | -6784 | 2533134
2026-07-16 | 2329493 | 3466430 | -136888 | 2466381
2026-07-17 | 2568457 | 3329542 | -84629 | 2653086
2026-07-18 | 2347202 | 3244913 | 99371 | 2247831
2026-07-19 | 2342796 | 3344284 | -108417 | 2451213
2026-07-20 | 2938379 | 3235867 | 253488 | 2684891
2026-07-21 | 2494576 | 3489355 | 3805 | 2490771
2026-07-22 | 2620298 | 3493160 | -75364 | 2695662
2026-07-23 | 2763702 | 3417796 | 40228 | 2723474
2026-07-24 | 2555610 | 3458024 | -7006 | 2562616
2026-07-25 | 2276918 | 3451018 | -143325 | 2420243
2026-07-26 | 2323502 | 3307693 | 88868 | 2234634
2026-07-27 | 2655077 | 3396561 | 35731 | 2619346
2026-07-28 | 2581041 | 3432292 | 30096 | 2550945
2026-07-29 | 2625102 | 3462388 | -21415 | 2646517
2026-07-30 | 2493932 | 3440973 | 54986 | 2438946
2026-07-31 | 2538533 | 3495959 | -41389 | 2579922
2026-08-01 | 2190702 | 3454570 | -167206 | 2357908
2026-08-02 | 2181212 | 3287364 | 85572 | 2095640
2026-08-03 | 2951844 | 3372936 | 125171 | 2826673
2026-08-04 | 2555218 | 3498107 | -56203 | 2611421
2026-08-05 | 2687998 | 3441904 | 20148 | 2667850
2026-08-06 | 2530456 | 3462052 | 44579 | 2485877
2026-08-07 | 2546700 | 3506631 | -60606 | 2607306
2026-08-08 | 2298017 | 3446025 | -149827 | 2447844
2026-08-09 | 2126508 | 3296198 | 90100 | 2036408
2026-08-10 | 2355508 | 3386298 | 31385 | 2324123
2026-08-11 | 2311311 | 3417683 | -69098 | 2380409
2026-08-12 | 2555186 | 3348585 | -82044 | 2637230
2026-08-13 | 2539863 | 3266541 | 133449 | 2406414
2026-08-14 | 2554321 | 3399990 | -42797 | 2597118
2026-08-15 | 2005706 | 3357193 | -51883 | 2057589
2026-08-16 | 2593167 | 3305310 | 112866 | 2480301
2026-08-17 | 2897613 | 3418176 | 1195 | 2896418
2026-08-18 | 2631949 | 3419371 | -247676 | 2879625
2026-08-19 | 3514361 | 3171695 | -87161 | 3601522
2026-08-20 | 3716646 | 3084534 | -752881 | 4469527
2026-08-21 | 4136417 | 2331653 | 436879 | 3699538
2026-08-22 | 3568590 | 2768532 | 410784 | 3157806
2026-08-23 | 3313133 | 3179316 | -117652 | 3430785
2026-08-24 | 3620398 | 3061664 | -136998 | 3757396
2026-08-25 | 3710615 | 2924666 | 33156 | 3677459
2026-08-26 | 3684708 | 2957822 | -14672 | 3699380
2026-08-27 | 3634142 | 2943150 | 106412 | 3527730
2026-08-28 | 3577451 | 3049562 | -166287 | 3743738
2026-08-29 | 3735008 | 2883275 | 613202 | 3121806
2026-08-30 | 3039398 | 3496477 | -62731 | 3102129
2026-08-31 | 3456496 | 3433746 | 40425 | 3416071
2026-09-01 | 3444357 | 3474171 | -48559 | 3492916
2026-09-02 | 3595723 | 3425612 | -690 | 3596413
2026-09-03 | 3545008 | 3424922 | 27202 | 3517806
2026-09-04 | 3429580 | 3452124 | 26562 | 3403018
2026-09-05 | 3238457 | 3478686 | -18226 | 3256683
2026-09-06 | 2999222 | 3460460 | -160276 | 3159498
2026-09-07 | 3538172 | 3300184 | 206908 | 3331264
2026-09-08 | 3537387 | 3507092 | -141492 | 3678879
2026-09-09 | 3531379 | 3365600 | 84465 | 3446914
2026-09-10 | 3585264 | 3450065 | -35584 | 3620848
2026-09-11 | 3462133 | 3414481 | 69074 | 3393059
2026-09-12 | 3096416 | 3483555 | -30290 | 3126706
2026-09-13 | 2845177 | 3453265 | -89352 | 2934529
2026-09-14 | 3668395 | 3363913 | 70947 | 3597448
2026-09-15 | 3453968 | 3434860 | 43785 | 3410183
2026-09-16 | 3537924 | 3478645 | -115895 | 3653819
2026-09-17 | 3577604 | 3362750 | 104872 | 3472732
2026-09-18 | 3355029 | 3467622 | 36304 | 3318725
2026-09-19 | 3053032 | 3503926 | -842 | 3053874
2026-09-20 | 2789966 | 3503084 | -185308 | 2975274
2026-09-21 | 3553084 | 3317776 | 152852 | 3400232
2026-09-22 | 3322390 | 3470628 | -51421 | 3373811
2026-09-23 | 3324652 | 3419207 | 63419 | 3261233
2026-09-24 | 3429502 | 3482626 | 3676 | 3425826
2026-09-25 | 3443329 | 3486302 | -3077 | 3446406
2026-09-26 | 3055483 | 3483225 | 20480 | 3035003
2026-09-27 | 2713614 | 3503705 | -83965 | 2797579
2026-09-28 | 3269291 | 3419740 | -42335 | 3311626
2026-09-29 | 3323930 | 3377405 | 8356 | 3315574
2026-09-30 | 3232255 | 3385761 | 29187 | 3203068
Year | 1021227830 |  | -51119 | 1021278949

## Wells
Well | Most recent pump test | Tested capacity (gpm) | In firm capacity
Well 1 (Field House) | 2026-09-15 | 1090 | No, largest well
Well 2 (Orchard) | 2026-04-22 | 820 | Yes
Well 3 (Recreation Fields) | 2026-05-12 | 760 | Yes
Well 4 (South Farm) | 2026-04-28 | 700 | Yes
Well 5 (Poultry Lane) | 2026-05-13 | 640 | Yes
Firm capacity |  | 2920

## Notes
Evaluation period: 1 October 2025 to 30 September 2026; days run midnight to midnight, Eastern time.
Well production: each well's discharge meter totalizer at the day's two midnights (daily log); the Well 3 register rolled over on 4 March 2026 and is counted through.
Storage: each tank's level at the day's two midnights (SCADA historian, hourly samples, UTC) times its gallons per foot of level (facilities summary), summed over Tanks A to D.
Water used on a day: production less the change in storage; it includes the water lost from the mains.
Capacities in gpm: gallons a day divided by 1,440. The capacity to add is the gap rounded up to a whole gpm.
Prepared by Campus Utilities, October 2026.