## Assessment
Tulrohan Block, outdoor air per occupant present, autumn term 2026
Outdoor air supplied, litres per second per occupant present | 5
TGD-M4 requirement 4.2, litres per second per person | 8
Shortfall against the requirement, litres per second per occupant present | 3
Teaching spaces in the block below the requirement | 6 of 6
Timetabled sessions assessed, 28 Sep to 11 Dec 2026 | 1728
Occupant-hours present across those sessions | 70404.6
Shortest response time in the block, volume over supply, minutes | 191
Length of a teaching period, minutes | 55
Recommendation for the January minor works allocation | Option A, replace AHU-03 and AHU-04 and the Tulrohan supply and extract distribution

## Occupied hours by month
Room | Block | Month | Occupied hours recorded | Occupied hours above 1,500 ppm
ANG-012 | Annagloor | September 2026 | 22.42 | 0
ANG-012 | Annagloor | October 2026 | 118.33 | 0
ANG-012 | Annagloor | November 2026 | 148.17 | 0
ANG-012 | Annagloor | December 2026 | 59.67 | 0
ANG-016 | Annagloor | September 2026 | 22.5 | 0
ANG-016 | Annagloor | October 2026 | 127.5 | 0
ANG-016 | Annagloor | November 2026 | 127.5 | 0
ANG-016 | Annagloor | December 2026 | 59.92 | 0
ANG-103 | Annagloor | September 2026 | 21.58 | 0
ANG-103 | Annagloor | October 2026 | 117.83 | 0.08
ANG-103 | Annagloor | November 2026 | 140 | 0.08
ANG-103 | Annagloor | December 2026 | 59 | 0
ANG-107 | Annagloor | September 2026 | 21.67 | 0
ANG-107 | Annagloor | October 2026 | 117.58 | 0
ANG-107 | Annagloor | November 2026 | 147.92 | 0
ANG-107 | Annagloor | December 2026 | 59.42 | 0
DRM-104 | Drumlusk | September 2026 | 22.17 | 0.17
DRM-104 | Drumlusk | October 2026 | 119.25 | 1
DRM-104 | Drumlusk | November 2026 | 148.67 | 1.08
DRM-104 | Drumlusk | December 2026 | 59.42 | 0.5
DRM-108 | Drumlusk | September 2026 | 22.5 | 0
DRM-108 | Drumlusk | October 2026 | 126.33 | 0.75
DRM-108 | Drumlusk | November 2026 | 141.58 | 0.5
DRM-108 | Drumlusk | December 2026 | 59.17 | 0.5
DRM-205 | Drumlusk | September 2026 | 22.33 | 0
DRM-205 | Drumlusk | October 2026 | 118.83 | 0.58
DRM-205 | Drumlusk | November 2026 | 140.67 | 0.5
DRM-205 | Drumlusk | December 2026 | 59.5 | 0.17
DRM-211 | Drumlusk | September 2026 | 21.75 | 0
DRM-211 | Drumlusk | October 2026 | 125.67 | 0.42
DRM-211 | Drumlusk | November 2026 | 140.67 | 0.42
DRM-211 | Drumlusk | December 2026 | 52.17 | 0.08
TUL-F04 | Tulrohan | September 2026 | 18.5 | 0.42
TUL-F04 | Tulrohan | October 2026 | 104.17 | 2.17
TUL-F04 | Tulrohan | November 2026 | 116.58 | 2.67
TUL-F04 | Tulrohan | December 2026 | 49.33 | 0
TUL-F09 | Tulrohan | September 2026 | 18.33 | 0
TUL-F09 | Tulrohan | October 2026 | 102.67 | 0
TUL-F09 | Tulrohan | November 2026 | 114 | 0
TUL-F09 | Tulrohan | December 2026 | 48.5 | 0
TUL-F15 | Tulrohan | September 2026 | 18.42 | 0.33
TUL-F15 | Tulrohan | October 2026 | 98.25 | 0.08
TUL-F15 | Tulrohan | November 2026 | 122.67 | 0.08
TUL-F15 | Tulrohan | December 2026 | 42.75 | 0.42
TUL-G07 | Tulrohan | September 2026 | 18.08 | 0
TUL-G07 | Tulrohan | October 2026 | 103.25 | 0.58
TUL-G07 | Tulrohan | November 2026 | 115 | 1
TUL-G07 | Tulrohan | December 2026 | 48.33 | 0
TUL-G12 | Tulrohan | September 2026 | 18.5 | 1.08
TUL-G12 | Tulrohan | October 2026 | 98.5 | 18.67
TUL-G12 | Tulrohan | November 2026 | 123.08 | 18.67
TUL-G12 | Tulrohan | December 2026 | 49.17 | 9.67
TUL-G18 | Tulrohan | September 2026 | 18.42 | 0
TUL-G18 | Tulrohan | October 2026 | 98.5 | 0.5
TUL-G18 | Tulrohan | November 2026 | 123 | 1.08
TUL-G18 | Tulrohan | December 2026 | 43 | 0.75

## Data capture
Room | Block | Readings received | Readings expected | Capture share %
ANG-012 | Annagloor | 13382 | 13824 | 96.8
ANG-016 | Annagloor | 12953 | 13824 | 93.7
ANG-103 | Annagloor | 13008 | 13824 | 94.1
ANG-107 | Annagloor | 13326 | 13824 | 96.4
DRM-104 | Drumlusk | 13437 | 13824 | 97.2
DRM-108 | Drumlusk | 13409 | 13824 | 97
DRM-205 | Drumlusk | 13119 | 13824 | 94.9
DRM-211 | Drumlusk | 13064 | 13824 | 94.5
TUL-F04 | Tulrohan | 13478 | 13824 | 97.5
TUL-F09 | Tulrohan | 13257 | 13824 | 95.9
TUL-F15 | Tulrohan | 13160 | 13824 | 95.2
TUL-G07 | Tulrohan | 13285 | 13824 | 96.1
TUL-G12 | Tulrohan | 13520 | 13824 | 97.8
TUL-G18 | Tulrohan | 13216 | 13824 | 95.6

## Session occupancy
Room | Timetabled sessions | Mean occupants present per session
TUL-G07 | 288 | 35
TUL-G12 | 288 | 48
TUL-G18 | 288 | 37
TUL-F04 | 288 | 49
TUL-F09 | 288 | 41
TUL-F15 | 288 | 56

## Largest session rises
Rank | Room | Date | Period
1 | TUL-G12 | 2026-11-02 | P1
2 | TUL-G12 | 2026-10-19 | P1
3 | TUL-G07 | 2026-10-13 | P2
4 | TUL-G12 | 2026-11-09 | P1

## Basis
Item | Basis used
Assessed period | 28 September to 11 December 2026, the autumn term's timetabled sessions
Population | the six Tulrohan Block rooms in the minor works bid scope
Denominator | the persons the attendance register marks present, in whichever role, procedure note EST-14 section 4
Occupied hours | the hours the serving air handling unit stands in its occupied state, procedure note EST-14 section 3
Readings expected | 288 a day on the 48 teaching days of the term, procedure note EST-14 section 3
Outdoor baseline | the campus analyser, and the Mace Head station for 12 to 25 October while the campus analyser was away
Rounding | once at the point of reporting, procedure note EST-14 section 5
Source of volumes | as-built room data sheets, project 19-0442 issue D
Extract pulled | 2026-12-15