## Programme
Losses programme 2027/28: fund the Kestle reconductoring
Copsewell Cross 11 kV feeders. Losses each project's replacement conductor would have removed in 2025/26, for the investment review panel of 9 December 2026. Network losses strategy (Gail Dobson), 30 November 2026.
| Feeder | Breaker | Sections replaced | Route replaced (km) | Existing conductor | Replacement | Saving 2025/26 (MWh) | Value at GBP 64.80/MWh (GBP)
Fund | Kestle | CB 7 | HV-21955, HV-22035, HV-22108 | 3.95 | 0.1 sq in hard-drawn copper | 200 mm2 AAAC (Elm) | 74.2 | 4800
Runner-up | Copsewell Town | CB 3 | HV-20543, HV-20609 | 1.18 | 0.1 sq in copper, paper-insulated lead-covered, 3-core | 300 mm2 aluminium, XLPE, triplex | 48.2 | 3100
| Redburn | CB 10 | HV-23137, HV-23164 | 4.05 | 0.1 sq in copper, paper-insulated lead-covered, 3-core | 300 mm2 aluminium, XLPE, triplex | 22.6 | 1500
| Pennick Hill | CB 9 | HV-22654, HV-22671 | 4.1 | 0.1 sq in copper, paper-insulated lead-covered, 3-core | 300 mm2 aluminium, XLPE, triplex | 19.9 | 1300
| Stowmere | CB 12 | HV-23616, HV-23664 | 4.43 | 50 mm2 ACSR (Rabbit) | 150 mm2 AAAC (Ash) | 17.5 | 1100
| Oxenford Lane | CB 6 | HV-21643, HV-21711 | 4.14 | 0.04 sq in hard-drawn copper | 150 mm2 AAAC (Ash) | 8.9 | 600
| Ashlade | CB 4 | HV-21142, HV-21184 | 2.02 | 0.15 sq in copper, paper-insulated lead-covered, 3-core | 300 mm2 aluminium, XLPE, triplex | 7.7 | 500
| Ingle Road | CB 13 | HV-23986, HV-24053 | 1.89 | 0.2 sq in copper, paper-insulated lead-covered, 3-core | 300 mm2 aluminium, XLPE, triplex | 4.2 | 300
Kestle saves 74.2 MWh a year against 48.2 for Copsewell Town, 26.0 MWh more.
Kestle's replaced overhead line carries the Hob Moor Solar Park's export back toward the Kestle Park estate near the primary, so most of its saving falls in the summer half-year.
Savings to one decimal place of a MWh, ranked on the unrounded figures; values to the nearest GBP 100. Basis on the next sheet.

## Basis
Year | The 17,520 half-hours from 00:00 on 1 April 2025 to 24:00 on 31 March 2026, UK time.
Saving | For each half-hour and each replaced section, the I2R loss at the current the section carried, on the existing conductor less on the replacement, summed over the project's sections and the year.
Section current | Each section's half-hourly current is the net of every connection beyond it on the feeder's normal running arrangement: each secondary substation's monitored load and each HV customer's settlement import less its export, balanced across three phases at 11 kV nominal.
Resistance | EDS 02-0310 issue 7, resistance at 20 C; nothing added for the network's own losses or voltage drop.
Value | Saving for the year at the 2027/28 losses value of GBP 64.80 per MWh.
Source | 2025/26 secondary substation monitoring, HV settlement data and the network model, extracted 12 June 2026.