## 2027 program
2027 underground cable program: Quarry Hill 21
Distribution Asset Management, Tamsin Valley district. Prepared 9 October 2026 from the October 2026 extract (records through 30 September 2026).
Feeder for the 2027 program | Quarry Hill 21
Basis | Expected failures of the cable itself (insulation, splice, termination) in calendar 2027 on the sections in service at 30 September 2026, damage by others left out
Method | Each section's failure rate for the number of cable failures it has already had (0, 1, 2, 3 or more), estimated on every section year since January 2012, summed over the feeder's sections
Why not the five-year counts | Mill Lane 7's recent failures are first failures on different sections, which rarely fail again; Quarry Hill 21 is the only feeder with in-service sections that have failed twice or more (the State Route 443 crossing)

## Feeders
Feeder | Circuit | Substation | UG sections in service | In-service sections with 2+ failures | Expected cable failures 2027 | Customers served 30 Sep 2026 | SAIFI RY2026 (MED excl.) | SAIDI RY2026, min (MED excl.) | Customers with 4+ sustained interruptions
Harrow Road 12 | 13-2412 | Harrow Road | 440 | 0 | 9.9 | 3878 | 1.4 | 71.3 | 108
Harrow Road 14 | 13-2414 | Harrow Road | 378 | 0 | 8.2 | 3105 | 1.97 | 131.4 | 1163
Mill Lane 3 | 13-3103 | Mill Lane | 344 | 0 | 7.5 | 4168 | 1.73 | 88.2 | 445
Mill Lane 7 | 13-3107 | Mill Lane | 364 | 0 | 7.9 | 3971 | 1.31 | 85.7 | 485
Quarry Hill 21 | 13-4421 | Quarry Hill | 307 | 17 | 15 | 2781 | 1.58 | 92.4 | 262
Quarry Hill 22 | 13-4422 | Quarry Hill | 248 | 0 | 5.5 | 3306 | 1.52 | 73.5 | 44
Sutter Park 5 | 13-5505 | Sutter Park | 346 | 0 | 7.6 | 3650 | 2.23 | 139.7 | 1812
Sutter Park 9 | 13-5509 | Sutter Park | 308 | 0 | 6.9 | 3362 | 1.53 | 125.5 | 65
District |  |  | 2735 | 17 |  | 28221
Expected failures are model estimates for ranking the feeders; the SAIFI, SAIDI and 4+ counts are the reliability year 1 Oct 2025 to 30 Sep 2026 under TVE-RS-04 rev 6.

## Failure rates
Cable failures already on the section | Section years at risk | Failures | Failures per section year
None | 37507.1 | 841 | 2.24%
One | 2730.2 | 55 | 2.01%
Two | 48.2 | 15 | 31.11%
Three or more | 44.9 | 26 | 57.86%
Section years from January 2012 (start of the work order archive) to 30 September 2026, split at each failure; INS, SPL and TRM work orders only.

## Notes
Notes
1. Cable failures: work orders with cause INS, SPL or TRM (wo_cause_repair_codes.csv); TPD (damage by others) and OTH left out.
2. Sections in service: status IS in the GIS export as of 30 September 2026; a section's failures stay with it, and a replacement section starts its own record.
3. Reliability year RY2026: 1 October 2025 to 30 September 2026, Eastern local time. ADMS times (UTC) converted before assigning days.
4. Sustained interruption: more than five minutes for the customer, timed to that customer's own restoration step (TVE-RS-04 3.3); customers served from the connectivity model on 30 September 2026 (3.2).
5. Major event days RY2026 (2.5 beta, threshold 13.72 min of daily SAIDI from RY2021 to RY2025): 25 Jan 2026, 28 Jul 2026. Left out of SAIFI and SAIDI, kept in the 4+ count (TVE-RS-04 6.1).
6. Substation bank outages counted once per customer on each feeder, not at the outage totals the OMS export repeats on each feeder row.