## Lost production 2025-26
Turbine | Downtime (MWh) | Grid curtailment (MWh) | Total (MWh)
CH01 | 60 | 292 | 352
CH02 | 47 | 297 | 344
CH03 | 103 | 297 | 400
CH04 | 130 | 293 | 423
CH05 | 51 | 302 | 353
CH06 | 430 | 291 | 721
CH07 | 56 | 302 | 358
CH08 | 129 | 304 | 433
CH09 | 341 | 300 | 641
CH10 | 71 | 302 | 373
Farm

## Campaign 2027
Turbine | Shortfall against warranted curve, same mean wind (MWh) | Blade loss at the same turbulence (MWh) | Normal-operation energy (MWh)
CH01 | 115 | 0 | 7604
CH02 | 71 | 65 | 7663
CH03 | 3 | 0 | 7420
CH04 | 93 | 89 | 7112
CH05 | 114 | 0 | 7235
CH06 | 4 | 0 | 5984
CH07 | 235 | 0 | 7196
CH08 | 2 | 0 | 6280
CH09 | -3 | 0 | 2017
CH10 | 8 | 0 | 6361
Campaign: CH04; energy recovered over the twelve months after the work 100 MWh (to the nearest 50 MWh).

## Notes
Twelve months October 2025 to September 2026 (UK local months). Lost production by OM-07 revision 3, section 4: the warranted power at the met mast's density-corrected 80 m wind, less the turbine's power, never negative, by ten-minute interval.
Downtime: faults, repairs and planned service, including the hours a controller was isolated for service or repair (from the work orders; the SCADA has no rows for them). Grid curtailment: intervals with an ANM instruction in force, other than downtime and stops for ice, high wind or grid loss.
SCADA timestamps: UK local time to 3 February 2026 (site server), UTC after (hosted platform).
Figures rounded to the nearest MWh from unrounded interval sums; the farm total is the sum of the rounded turbine figures.
Prepared by Jenna Dyer, Asset Manager, Cairnhollow Community Energy, 14 October 2026.