## Volume 2027
Hadley Ranch Solar: 2027 forward sale at the one-year P90
Energy and commodities desk, for the treasurer's approval, October 2026
Volume to sell forward for 2027 (MWh) | 70000 | one-year P90 rounded down to the nearest 1,000 MWh (policy 4.1)
P50 (MWh) | 73000 | mean of the 25 weather-year outputs, to the nearest 1,000 MWh
Standard deviation (MWh) | 1900 | sample standard deviation of the 25 weather-year outputs, to the nearest 100 MWh
Performance build
Performance ratio, October 2025 to September 2026 | 63.7 | per cent: net export at the revenue meter over plane-of-array irradiation times 40,320 kWp
Original modules' own wear since 2016 | 14 | per cent: fall in DC energy per kWp per kWh/m2 at the inverters' DC input, temperature-corrected, on the days after each block's wash
Side-by-side gain, CV-450BHC over unexposed KS-315P | 14.7 | per cent: twelve months' DC energy per kWp, Corvane report FA-2026-114
Performance ratio of the repowered plant | 85 | per cent: base-period ratio restored by the wear alone, times the gain
Repowered DC capacity (kWp) | 37324.8 | 82,944 CV-450BHC modules of 450 W
Losses the plant keeps in 2027: the inverters' conversion losses and outages, and the dust between December washes under the current O&M agreement, all as in the base period.

## Weather years
Weather year | Plane-of-array irradiation (kWh/m2) | 2027 output (MWh)
2001 | 2313.2 | 73200
2002 | 2325 | 73600
2003 | 2288.3 | 72400
2004 | 2389.8 | 75600
2005 | 2350.9 | 74400
2006 | 2290.9 | 72500
2007 | 2361.8 | 74700
2008 | 2331.8 | 73800
2009 | 2353.2 | 74500
2010 | 2271.7 | 71900
2011 | 2376.9 | 75200
2012 | 2203.1 | 69700
2013 | 2300.6 | 72800
2014 | 2237.5 | 70800
2015 | 2317.4 | 73300
2016 | 2267.5 | 71700
2017 | 2300.2 | 72800
2018 | 2350.8 | 74400
2019 | 2406.6 | 76200
2020 | 2327.3 | 73600
2021 | 2188 | 69200
2022 | 2358 | 74600
2023 | 2167.7 | 68600
2024 | 2340 | 74000
2025 | 2325.1 | 73600
P50 |  | 73000
Standard deviation |  | 1900
Volume (P90, rounded down) |  | 70000

## Inverter availability 2025
Inverter | Production hours | Unavailable hours | Excluded hours | Availability (%)
B1-INV1 | 3981 | 60 | 12 | 98.49
B1-INV2 | 3981 | 96 | 12 | 97.58
B1-INV3 | 3981 | 87 | 12 | 97.81
B1-INV4 | 3981 | 94 | 12 | 97.63
B2-INV1 | 3981 | 48 | 7 | 98.79
B2-INV2 | 3981 | 14 | 7 | 99.65
B2-INV3R | 3981 | 74 | 7 | 98.14
B2-INV4 | 3981 | 131 | 7 | 96.7
B3-INV1 | 3981 | 68 | 13 | 98.29
B3-INV2 | 3981 | 7 | 13 | 99.82
B3-INV3 | 3981 | 28 | 13 | 99.29
B3-INV4 | 3981 | 106 | 13 | 97.33
B4-INV1 | 3981 | 29 | 7 | 99.27
B4-INV2 | 3981 | 56 | 7 | 98.59
B4-INV3 | 3981 | 114 | 7 | 97.13
B4-INV4 | 3981 | 113 | 7 | 97.16
Schedule 4 of the O&M agreement: Excluded Hours are the district's 69 kV interruptions and the stops the owner requested.

## Hedge record 2016-2025
Year | Net energy at the delivery point (MWh) | Volume sold forward (MWh) | Over (+) or under (-) (MWh)
2016 | 73020 | 69000 | 4020
2017 | 73582 | 67000 | 6582
2018 | 71815 | 67000 | 4815
2019 | 69564 | 65600 | 3964
2020 | 63077 | 66000 | -2923
2021 | 56034 | 55500 | 534
2022 | 60636 | 50900 | 9736
2023 | 56570 | 52000 | 4570
2024 | 60284 | 50200 | 10084
2025 | 59715 | 52000 | 7715
Delivery point: district service point 0417 (REC less DEL). Volumes net of the 2019 and 2022 buy-backs, with the 2021 and 2024 amendments.

## Notes
Sources | Plant SCADA daily exports (original system to March 2, 2020; replacement system from March 3, 2020), pulled October 6, 2026; Tresco work orders; Corvane report FA-2026-114; Clearfield site-adapted hourly series 2001 to 2025 (delivered January 2026); module replacement scope, July 2026.
Base period | October 1, 2025 to September 30, 2026, the twelve complete months before the sale (energy risk policy, section 4.4).
Performance ratio | Net export at the revenue meter (SCADA PLANT-RM export less import) over plane-of-array irradiation times DC nameplate.
Wear | Days 1 to 3 after each block's wash in the CLN work orders, inverters with full operating hours; DC energy at the inverter input per kWp per kWh/m2, corrected to 25 degC at -0.42 per cent per degC on the irradiance-weighted module temperature (KS-315P datasheet). 2016 against the December 2025 wash.
Weather years | Full calendar years 2001 to 2025 of the long-term record, Arizona time (policy section 4.2).
Rounding | Volume rounded down to the nearest 1,000 MWh from the unrounded P90 (policy section 4.1); P50 to the nearest 1,000 MWh, standard deviation to the nearest 100 MWh, weather-year outputs to the nearest 100 MWh.
Availability | O&M agreement Schedule 4, contract year 2025: Production Hours from the met station's hourly plane-of-array irradiance; an hour missing from the logger export counts as delivered where the inverter's AC register advanced across it.
Hedge record | Net energy at district service point 0417 (REC less DEL) from the legacy billing export to February 29, 2020 and the meter data system after it, latest version of each day; volumes from the blotter, with Westmark's amendments of the 2021 and 2024 confirmations.