## Call
YRB27 takes the FY2027-28 hosting-capacity augmentation: its rooftop PV sits furthest above hosting capacity at the 31 August 2029 design point
Yarrabin 22 kV feeders, forecast under NPP-114 rev 3 from a base date of 31 August 2026.
Feeder to receive the augmentation | YRB27
Rooftop PV above hosting capacity at 31 August 2029 (MW) | 1.9
Runner-up feeder | YRB24
Runner-up above hosting capacity (MW) | 1.4
Gap between them (MW) | 0.5
Solar Streets 2026, Bindarra Waters (YRB24): PV added (MW) | 0.4
Solar Streets 2026, Wattleview (YRB27): PV added (MW) | 1.7
YRB27's rooftop PV is forecast at 25.2 MW on 31 August 2029 against a 2029 hosting capacity of 23.30 MW; 1.7 MW of it is the Wattleview bulk-buy.
Past Solar Streets campaigns installed about 1.17 systems for every first application their suburb's owner-occupied houses lodged in the year before sign-ups opened (505 systems on 431 applications over the seven campaigns). That is the only basis on which the seven agree; per home letterboxed or per house without PV they vary several-fold (Solar Streets sheet).
Wattleview's owner-occupiers lodged 209 first applications in the year to August 2026 and Bindarra Waters' lodged 52, so Wattleview's campaign is expected to add about four times as much PV although Bindarra Waters has more houses still without it.

## Forecast
Forecast rooftop PV (micro EG) at 31 August 2029 by feeder
Feeder | Connected 31 Aug 2026 (kW) | Trend (kW a year, FY2023-24 to FY2025-26) | Base forecast 31 Aug 2029 (kW) | Solar Streets 2026 systems | Program capacity (kW) | Forecast 31 Aug 2029 (kW) | Hosting capacity, 2029 case (MW) | Above hosting capacity (MW) | Rank
YRB21 | 13600 | 776 | 15928 |  |  | 15928 | 14.82 | 1.1 | 4
YRB22 | 20336 | 1054 | 23499 |  |  | 23499 | 22.29 | 1.2 | 3
YRB23 | 10662 | 498 | 12157 |  |  | 12157 | 11.72 | 0.4 | 7
YRB24 | 4637 | 498 | 6130 | 60.9 | 396 | 6525 | 5.13 | 1.4 | 2
YRB25 | 4733 | 372 | 5851 |  |  | 5851 | 4.79 | 1.1 | 5
YRB26 | 10370 | 504 | 11884 |  |  | 11884 | 12.54 | -0.7 | 8
YRB27 | 17938 | 1852 | 23495 | 244.9 | 1707 | 25202 | 23.3 | 1.9 | 1
YRB28 | 10078 | 540 | 11698 |  |  | 11698 | 10.99 | 0.7 | 6
Yarrabin | 92355 | 6096 | 110642 | 305.8 | 2103 | 112744
Connected capacity: each NMI's latest connected configuration on the network model's feeder; trend: the yearly increase in connected capacity less program systems first connected that year; program systems at the feeder's FY2025-26 average inverter rating (NPP-114 3.2, 4.1 to 4.3). Systems are carried unrounded.

## Solar Streets
Solar Streets: what a campaign installs, carried from the seven past campaigns
Campaign | Suburb | Feeder | Sign-ups opened | First applications from owner-occupied houses, 12 months before sign-ups opened | Systems installed (program reference) | Systems per first application
GLM18 | Glenmorrow | YRB21 | 2018-09-03 | 16 | 19 | 1.19
KJP19 | Kurrajong Park | YRB22 | 2019-09-02 | 162 | 180 | 1.11
TWR21 | Tallowwood Rise | YRB25 | 2021-09-06 | 43 | 53 | 1.23
SKO22 | Silky Oak | YRB23 | 2022-03-07 | 81 | 109 | 1.35
IBH22 | Ironbark Hill | YRB28 | 2022-09-05 | 41 | 48 | 1.17
BNR23 | Bunya Ridge | YRB26 | 2023-09-04 | 33 | 34 | 1.03
PBG24 | Paperbark Grove | YRB21 | 2024-09-02 | 55 | 62 | 1.13
All seven |  |  |  | 431 | 505 | 1.172
Basis tried |  |  |  | Pooled rate over the seven | Lowest campaign | Highest campaign | Coefficient of variation
Per 100 homes letterboxed (the council's participation rate) |  |  |  | 1.94 | 0.6 | 4.38 | 0.72
Per 100 owner-occupied houses in the suburb |  |  |  | 3.34 | 1.3 | 5.98 | 0.61
Per 100 owner-occupied houses without PV when sign-ups opened |  |  |  | 6.1 | 2.33 | 13.9 | 0.71
Per first application from the suburb's owner-occupied houses in the 12 months before sign-ups opened |  |  |  | 1.172 | 1.03 | 1.346 | 0.09
2026 campaign | Suburb | Feeder | Sign-ups open | First applications from owner-occupied houses, 1 Sep 2025 to 31 Aug 2026 | Systems added | Average inverter (kW, FY2025-26) | PV added (MW)
BDW26 | Bindarra Waters | YRB24 | 2026-09-01 | 52 | 60.9 | 6.5 | 0.4
WTV26 | Wattleview | YRB27 | 2026-09-01 | 209 | 244.9 | 6.97 | 1.7
Owner-occupied house: rates roll land use 02 with rating R1, matched to NMIs through the GIS cross-reference. A first application is the earliest application at the NMI, other than a withdrawn one. Systems installed are the connected new systems lodged with the campaign's reference.

## DER Register
Active DER Register sites by feeder, extract as at 31 August 2026
Feeder | Active sites | Sites first lodged in FY2025-26 | Inverter capacity (kW) | Battery storage (kWh)
YRB21 | 2323 | 82 | 14000 | 1940
YRB22 | 3448 | 130 | 20680 | 2410
YRB23 | 1713 | 65 | 10860 | 1310
YRB24 | 702 | 68 | 4730 | 750
YRB25 | 717 | 44 | 4850 | 650
YRB26 | 1996 | 35 | 10830 | 1710
YRB27 | 2729 | 252 | 18040 | 2950
YRB28 | 1781 | 62 | 10340 | 1380
A site is the premises' NMI (ten characters; a builder's temporary supply NMI read at the NMI that replaced it), placed on the feeder the network model shows supplying it at 31 August 2026. First lodged: the earliest registration of any AC connection at the site, decommissioned ones included.
Inverter capacity: two-inverter connections lodged on the installer portal before July 2024 carry the connection's total on each inverter row and are counted once. Battery storage: Sungrow SBR stacks carry the stack's total on each module row and are counted once; other modular batteries are lodged module by module and summed. Rounded to the nearest 10 kW and 10 kWh.

## Notes
Notes and sources
Base date | 31 August 2026 (NPP-114 rev 3, clause 3.1); connection register extract of 1 September 2026 and the network model at 31 August 2026.
Design point | 31 August 2029, the start of the spring minimum-demand season (clause 2.4).
Rooftop PV | Micro EG of 30 kVA or less at residential and business NMIs, at the inverter's AC rating; systems migrated in 2019 take their inverters from the legacy equipment table.
Hosting capacity | Buchanan Power Engineering report BPE-2026-031 (24 July 2026), spring 2029 minimum-demand case (clause 5.1).
Solar Streets 2026 | Merindah City Council letter of 14 August 2026 (reference SS/2026/02): sign-ups 1 September to 27 November 2026 in Bindarra Waters and Wattleview.
Past campaigns | The council's Solar Streets summary, 2018 to 2024, for sign-up dates; systems counted from program references in the connection register, which agree with the council's systems installed for every campaign. The rate is pooled over the seven (clause 4.2).
DER Register | Extract as at 31 August 2026, AC connections and devices at NMIs on the Yarrabin feeders; the NMI re-allocation log for builders' temporary supply NMIs.
Rounding | Carried unrounded and rounded once: MW to one decimal (clause 7.1); inverter capacity to the nearest 10 kW and battery storage to the nearest 10 kWh.