## Allocation
Foothill takes 79 of the 400 replacements: 1,824 transformers forecast above 120% of nameplate for summer 2027
2027 Proactive Service Transformer Replacement Program, D.26-11-019 Ordering Paragraphs 2 to 5. Record date 31 March 2027.
District | Transformers at risk | Proportional share | Replacements
Foothill | 361 | 79.167 | 79
Railyard | 311 | 68.202 | 68
Canal | 224 | 49.123 | 49
Mission | 104 | 22.807 | 23
West Bluff | 72 | 15.789 | 16
Crestview | 19 | 4.167 | 4
Lakeside | 18 | 3.947 | 4
Sunrise | 14 | 3.07 | 3
Sandhill | 328 | 71.93 | 72
Kingsley | 118 | 25.877 | 26
Highland | 36 | 7.895 | 8
Brookside | 219 | 48.026 | 48
System | 1824 | 400 | 400
Forecast 2027 summer peak (OP 4): each transformer's recorded 2026 TLM peak, plus the effect of each vehicle registered at its service points on 31 March 2027, less that of each vehicle registered there on the day of its 2026 peak, each at its premise's schedule on that date. One effect per schedule: the mean rise in recorded peak of the transformers that gained one vehicle on that schedule and nothing else between the 2024, 2025 and 2026 summers, weather-adjusted by the district's median ratio on transformers with no change.
At risk: forecast above 1.2 times the GIS kVA rating of the unit installed on the record date. Shares to 400 by largest remainder (OP 2). Registrations dated 1 to 4 April 2027 in the 5 April DMV feed are after the record date and not counted.
Effect of one vehicle on a transformer's recorded summer peak, kVA
Vehicle at a service point on | kVA per vehicle
Schedule R-EV2 | 0.88369
Other residential schedules | 4.9218

## Pilot close-out
2025-26 pilot: 263 transformers replaced in Railyard, Canal and Brookside
Decision 25-06-011 pilot, work completed 6 October 2025 to 24 April 2026. Charges to internal order 7100-PTR25 at 5 April 2027.
District | Transformers replaced | Nameplate kVA added | Charges to pilot work orders ($) | Cost per transformer replaced ($)
Railyard | 94 | 1812.5 | 639109.06 | 6799
Canal | 81 | 1532.5 | 570949.57 | 7049
Brookside | 88 | 1615 | 616682.88 | 7008
Replaced: PTR changes in GIS whose installed serial differs from the removed serial, second units set under another unit's order included. 4 Railyard, 8 Canal and 4 Brookside units on the screen were found larger on the pole than GIS recorded; their records were corrected under pilot orders and they are not counted. Charges include cancelled and no-work orders, net of reversals.

## Summer 2026 failures
Transformer failures cost 12,356 customer-hours between 1 June and 30 September 2026
OMS outage lines, cause EQ-XFMR, outage start in the window in local time (PDT, UTC less 7 hours).
District | Customer-hours | Customers out more than 8 hours
Foothill | 1010 | 50
Railyard | 1676 | 80
Canal | 1185 | 54
Mission | 1231 | 52
West Bluff | 810 | 42
Crestview | 717 | 39
Lakeside | 540 | 21
Sunrise | 1181 | 41
Sandhill | 1527 | 87
Kingsley | 1063 | 35
Highland | 764 | 18
Brookside | 652 | 35
System | 12356 | 554
Each outage line is counted at its own transformer's service points: the OMS customers_out field repeats the event's total on every line of an event that took a tap or loop fuse. Hours run from the outage start to the line's restoration; district from the GIS register.

## Notes
Prepared for the D.26-11-019 Tier 2 advice letter due 30 April 2027.
Extracts pulled 5 April 2027: TLM season runs 2024 to 2026, GIS register and unit changes, service points, rate schedule changes, DMV plug-in vehicle notifications, OMS outage lines, pilot work orders and cost lines.
Districts are operating districts in the GIS register on the record date.
Rounding: kVA to one decimal, cost to the nearest dollar, customer-hours to the nearest whole hour; shares to three decimals for reference.