## Metered generation
Turbine | Metered generation (MWh)
CH01 | 6708
CH02 | 6770
CH03 | 6554
CH04 | 6327
CH05 | 6404
CH06 | 5966
CH07 | 6394
CH08 | 6398
CH09 | 5938
CH10 | 6394
Farm

## Metered export
Month | Metered export (MWh)
2025-11 | 6960
2025-12 | 9765
2026-01 | 5121
2026-02 | 6819
2026-03 | 8310
2026-04 | 5868
2026-05 | 2513
2026-06 | 3267
2026-07 | 5634
2026-08 | 6334
Ten months

## Campaign 2027
Turbine | Shortfall against warranted curve, same mean wind (MWh) | Blade loss at the same turbulence (MWh) | Normal-operation energy (MWh)
CH01 | 115 | 0 | 7604
CH02 | 71 | 65 | 7663
CH03 | 3 | 0 | 7420
CH04 | 93 | 89 | 7112
CH05 | 114 | 0 | 7235
CH06 | 4 | 0 | 5984
CH07 | 235 | 0 | 7196
CH08 | 2 | 0 | 6280
CH09 | -3 | 0 | 2017
CH10 | 8 | 0 | 6361
Campaign: CH04; energy recovered over the twelve months after the work 100 MWh (to the nearest 50 MWh).

## Notes
Twelve months October 2025 to September 2026 (UK local months). Lost production by OM-07 revision 3, section 4: the warranted power at the met mast's density-corrected 80 m wind, less the turbine's power, never negative, by ten-minute interval.
Downtime: faults, repairs and planned service, including the hours a controller was isolated for service or repair (from the work orders; the SCADA has no rows for them). Grid curtailment: intervals with an ANM instruction in force, other than downtime and stops for ice, high wind or grid loss.
SCADA timestamps: UK local time to 3 February 2026 (site server), UTC after (hosted platform).
Figures rounded to the nearest MWh from unrounded interval sums; the farm total is the sum of the rounded turbine figures.
Prepared by Jenna Dyer, Asset Manager, Cairnhollow Community Energy, 14 October 2026.