## Phase 3 2027-28
Phase 3 falls 0.07 Ml/d short of its contracted 0.48 Ml/d in 2027-28: add 2 find-and-fix gang-years
Leakage Outcome Contract LW/LOC/2024/07, Schedule 4 (Variation 3): the 22 Phase 3 districts, NZ13 to NZ34, with fixed-outlet PRVs at the rev C settings from 1 April 2027
| Value | Unit
2025-26 assessed leakage (Lynmere export of 14 May 2026) | 3.22 | Ml/d
2027-28 forecast leakage | 2.81 | Ml/d
Reduction | 0.41 | Ml/d
Contracted reduction (Schedule 4.3) | 0.48 | Ml/d
Shortfall | 0.07 | Ml/d
Find-and-fix gang-years to add for 2027-28 (Schedule 4.4) | 2 | gang-years
Forecast: each district's 2025-26 hourly inlet and average zone pressures replayed through its valve, the outlet the lower of the inlet pressure and the setting and the zone pressure lowered by the same amount; net night flow scaled to the replayed AZNP at the district's N1 (LW-LA-04 Table C2), night-day factor rebuilt from the replayed pressures, day by day, then LW-LA-04's months and year.
On weekdays from about 06:00 to 22:00 the paper mill's draw on the trunk main takes the far districts' inlets below their settings and the valves stand open. Carrying each valve's night pressure ratio through the whole day would show a 0.63 Ml/d reduction.
Conditions as Clive Heath's note of 19 October 2026: each month as recorded in the same month of 2025-26, no growth. Gang-years at 0.05 Ml/d each, rounded up.

## Other districts 2025-26
The zone's twelve other districts: 2025-26 assessed leakage by LW-LA-04 issue 6
The districts nearer Thornholme, outside Phase 3, from their own inlet meters and average zone points
District | Name | Leakage (Ml/d)
NZ01 | Orlesby Village | 0.153
NZ02 | Kessington Lane | 0.127
NZ03 | Halverby Park | 0.164
NZ04 | Wrenfold | 0.138
NZ05 | Stainmoor Ings | 0.126
NZ06 | Kestle Road | 0.095
NZ07 | Sorrelby End | 0.209
NZ08 | Cragthwaite Top | 0.098
NZ09 | Linmere Green | 0.146
NZ10 | Barrowside | 0.146
NZ11 | Old Mill Fields | 0.101
NZ12 | Ravens Clough | 0.114
Night use allowed for each dwelling connected that day: a new build counts from its plot connection and once, its address record taking over on the same supply point; flats on a shared supply count one each.
NZ04: both inlet meters, the second still logged as NZ04A. NZ09 and NZ10 leave out 12 to 20 January 2026, when NZ09 was fed through boundary valve BV-0910.

## Zone balance 2025-26
Northern zone water balance, 2025-26 (LW-LA-04 section 8)
1 April 2025 to 31 March 2026, megalitres a day over the year's 365 days
Component | Ml/d
System input (Thornholme outlet meter TH-OUT-0417) | 30.36
Billed metered consumption | 18.11
Billed unmetered consumption | 5.61
Unbilled authorised use | 0.12
Apparent losses | 0.54
Real losses | 5.97
System input: daily outlet volumes before 12 November 2025 divided by 0.986 (as found 1.4 per cent low, certificate FFS-25-1182).
Customers: the properties in the zone's 34 districts (NZ04A mapped to NZ04) and the trunk main's direct supplies (NZ-TM); bills apportioned to the year by days.
Flats on a shared supply carry one assessed bill each, so a supply point can show identical lines.
The 34 districts' assessed leakage sits under these real losses, which also carry the trunk main's own losses and the balance's estimates.

## Sources
Sources
Telemetry | northern_zone_inlet_loggers_2025_26.csv and northern_zone_pressure_loggers_2025_26.csv, hourly means in GMT; logger_register.csv for serials, makes and units (1 bar = 10.197 m)
Baseline | dma_leakage_assessment_phase3_2025_26.xlsx, Lynmere export of 14 May 2026
Method | LW-LA-04 issue 6, effective 1 April 2025, with Table C2
Valves | phase3_prv_schedule_rev_C.xlsx, Coldbeck network modelling, 9 October 2026
Contract | outcome_contract_schedule_4_phase3.pdf, Variation 3 of 2 September 2026
Properties and bills | property_extract_2026-11-02.csv and billing_extract_north_2025_26.csv
Files taken | Monday 2 November 2026